SECTION 05430

SLOTTED CHANNEL FRAMING 

(STRUT SYSTEMS)

PART 1 - GENERAL

1.01
SECTION INCLUDES


A.
Continuous slot, bolted metal framing channels and all associated fittings and hardware.


B.
Trapeze type supports for cable tray, conduit, pipe and other similar systems.


C.
Use of bolted metal framing as a surface metal raceway.

1.02
REFERENCES


A.
ASTM A123 - Specification for Zinc (Hot-Galvanized) Coatings on Products Fabricated from Rolled, Pressed, and Forged Steel Shapes, Plates, Bars, and Strip


B.
ASTM A653 - General Requirements for Steel Sheet, Zinc-Coated Galvanized by the Hot-Dip Process 

C. ASTM A1011 - Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formablility (Formerly ASTM A570)
D. ASTM F1136 – Standard Specification for Chromium/Zinc Corrosion Protective Coatings for Fasteners

E. ASTM A907 - Standard Specification for Steel, Sheet and Strip, Heavy-Thickness Coils, Carbon, Hot-Rolled, Structural Quality

F. ASTM B633 - Specification for Electrodeposited Coatings of Zinc on Iron and Steel

G. MFMA - Metal Framing Manufactureres Association

H. ANSI/NFPA 70– National Fire Protection Association (National Electrical Code)

I. AISI - American Iron and Steel Institute

1.03
QUALITY ASSURANCE


A.
Manufacturers:  Firms regularly engaged in the manufacture of bolted metal framing of the types required, whose products have been in satisfactory use in similar service for not less than 5 years.


B.
MFMA Compliance:  Comply with the latest revision of MFMA Standards Publication Number MFMA-4, "Metal Framing Standards Publication".


C.
NEC Compliance:  Comply with the latest revision NFPA 70  - Article 352 "Surface Metal Raceways and Surface Nonmetallic Raceways".


D.
UL Compliance:  Comply with UL "Standard for Surface Metal Raceway and Fittings", UL 5.


E.
Bolted framing channels and fittings shall have the manufacturers name, part number, and material heat code identification number stamped in the part itself for identification.   Material certification sheets and test reports must be made available by the manufacturer upon request.


F.
Stainless steel bolted framing parts shall be stamped to identify the material.  Material certification sheets and test reports must be made available by the manufacturer upon request.

1.04
SUBMITTALS


A.
Submit drawings of strut and accessories including clamps, brackets, hanger rods, and fittings.


B.
Submit manufacturer's product data on strut channels including, but not limited to, types, materials, finishes, gauge thickness, and hole patterns.  For each different strut cross-section, submit cross sectional properties including Section Modulus (Sx) and Moment of Inertia (Ix).

1.05
DELIVERY, STORAGE, AND HANDLING


A.
Deliver strut systems and components carefully to avoid breakage, denting, and scoring finishes.  Do not install damaged equipment.


B.
Store strut systems and components in original cartons and in clean dry space; protect from weather and construction traffic.

PART 2 PRODUCTS

2.01
ACCEPTABLE MANUFACTURERS


A.
Manufacturer:  Subject to compliance with these specifications, strut systems to be installed shall be as manufactured by Cooper B-Line, Inc. [or engineer approved equal].

2.02
STRUT CHANNELS AND COMPONENTS


A.
General:  Strut shall be 1-5/8 inches wide in varying heights and welded combinations as required to meet load capacities and designs indicated on the drawings.


B.
Materials and Finish:  Material and finish specifications for each strut type are as follows:



1. 
Aluminum:  Strut shall be manufactured of extruded aluminum alloy 6063-T6.  All fittings and hardware shall be zinc plated according to ASTM B633 (SC3 for fittings, SC1 for threaded hardware) for indoor use only.  For outdoor use, all fittings and hardware shall be stainless steel Type 304 [Type 316].  [Fittings shall be hot dip galvanized after fabrication in accordance with ASTM 123 with stainless steel Type 304 [Type 316] or chromium zinc ASTM F1136 Gr. 3.]



2.
Epoxy Painted:  Strut shall be made from steel meeting the minimum mechanical properties of ASTM A1011 SS Grade 33, then painted with water born epoxy applied by a cathodic electro-deposition process.  Fittings shall be manufactured from steel meeting the minimum requirements of ASTM A907 SS, Grade 33.  All fittings and hardware shall be zinc plated in accordance with ASTM B633 (SC3 for fittings, SC1 for threaded hardware).



3.
Pre-galvanized Steel:  Strut shall be made from steel meeting the minimum mechanical properties of ASTM A653 SS, Grade 33, and mill galvanized in accordance with coating designation G90.  Fittings shall be manufactured from steel meeting the minimum requirements of ASTM A907 SS, Grade 33.  All fittings and hardware shall be zinc plated in accordance with ASTM B633 (SC3 for fittings, SC1 for threaded hardware).



4.

Hot-dip Galvanized Steel:  Strut shall be made from steel meeting the minimum mechanical properties of ASTM A1011 SS, Grade 33 and shall be hot-dip galvanized after fabrication in accordance with ASTM A123.  Fittings shall be manufactured from steel meeting the minimum requirements of ASTM A907 SS, Grade 33, and hot-dip galvanized after fabrication in accordance with ASTM A123.  All hardware shall be stainless steel Type 304 [Type 316] or chromium zinc ASTM F1136 Gr. 3.  All hot-dip galvanized after fabrication products must be returned to point of manufacture after coating for inspection and removal of all sharp burrs.



5.

Stainless Steel:  All strut, fittings and hardware shall be made of AISI Type 304 [Type 316] stainless steel as indicated.

PART 3 EXECUTION
3.01 INSTALLATION


A.
Install strut in accordance with MFMA-102 ‘Guidelines for the Use of Metal Framing’; in accordance with equipment manufacturer's recommendations, and with recognized industry practices.


B.
All nuts and bolts shall be tightened to the following values:







Bolt Size
Torque (ft-lbs)





     1/4 - 20


    6






    5/16 - 18


   11






     3/8 - 16


   19






     1/2 - 13


   50

END OF SECTION

(May also be cross-referenced from Sections 05450, 15060 & 16070)

Project Name / Project # / Date                                       05430 - 4                                                            Strut Systems

