[image: image1.png]OOOOOOOOOOOOOO




HPS Titan®
1.2kV Class 
Hazardous Location

(UL Listed, Class 1, Division 2, Groups A, B, C & D and class I, Zone 2, Group IIC, T3 Hazardous Location)
Encapsulated Distribution Transformer

Typical Specification
Canada
595 Southgate Drive

Guelph, Ontario
N1G 3W6
Phone: 1-888-798-8882
Fax: 1-519-822-9701
United States
1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com
1 GENERAL
1.1 SCOPE
A This section defines dry-type, encapsulated enclosed transformers as indicated. 
1.2 RELATED DOCUMENTS

A Drawing and general provisions of the Contract, including General and Supplementary Conditions and Specification Sections, apply to this Section
1.3 REFERENCES
A ANSI C57.12.01/NEMA ST 20-Dry Type Transformer For General Applications
B IEEE C57.110-1998

C UL certified (UL file number: E258346), CSA
D ANSI/ISA 12.12.10 – Class 1, Division 2, Groups A,B,C,D and Class I, Zone 2, Group IIC, T3 Hazardous Location
E ABS Type Approval for Marine Duty Service and Offshore Applications

1.4 SUBMITALS

A Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract. 
i Customer name. Customer location and customer order number shall identify all transmittals.

ii Product Data including KVA rating, Temperature Rise, Detailed enclosure dimensions, Primary & Secondary nominal voltages, primary voltage taps, no load & full load losses per NEMA ST20, impedances, unit weight, warranty.
1.5 STORAGE AND HANDLING
A Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and if necessary, apply temporary heat where required to obtain suitable service conditions.

B Handle transformer using proper equipment for lifting and handling, use when necessary lifting eye and/or brackets provided for that purpose.

1.6 WARRANTY
A The transformer shall carry a 10 year limited warranty.

(For details refer to the manufacturer’s published warranty)
2 PRODUCTS
2.1 General construction:

A All single phase and three phase transformers shall be encapsulated type. The primary side of each transformer shall, if applicable, be provided with taps that meet or exceed NEMA standards. 
B Transformers shall be designed, constructed and rated in accordance with UL, CSA, NEMA and ABS standards. If shipping to Europe, transformer will also have to be manufactured in accordance to CE standards and carry a CE mark.
2.2 Voltage and kVA Requirements:

A Primary Voltage:   Single Phase – [208/240/277][347/380][240X480][600][other] Volts
                                           Three Phase - [480][600][600/480][other] Volts
B Secondary Voltage: Single Phase - [120/240][other] Volts
                                              Three Phase - [208Y/120][240D][480Y/277][600Y/347][other] Volts
C kVA Rating:  Single Phase - [.05][.10][.15][.20][.25][.35][.50][.75][1][1.5][2][3][5][7.5]                  


      [10][15][25][37.5][other] kVA

        Three Phase – [2][3][6][9][15][30][45][75][112.5][150][other] kVA


D System Frequency:  60 [50][other] Hertz
2.3 Basic Requirements:
A Standard impedance at 60Hz:
2% to 5% (up to 10 kVA), 1% to 3% (above 10 kVA)

B Name Plate Rating:  Linear load, 60Hz
C Single-phase or three-phase, common core construction.  Convection air cooled.  

D Insulation Class:  [180°C][130°C][other].
E Temperature Rise:  [80°C][115°C][other].
F Taps:  [1 x ± 5% (1FCAN, 1FCBN)][2 x ± 2.5% (2FCAN, 2FCBN)][2 x +2.5%, 4 x -2.5% (2FCAN, 4FCBN)][2 x - 5% (2FCBN)][none][other].
G Core construction: high grade non-aging, fully processed silicon steel laminations or better.
H Coil conductors: copper windings, with terminations brazed, welded or bolted.
I Electrostatic Shielding on all single phase units over 0.50 kVA and all three phase units.
J Sound level to meet NEMA ST-20.
K Enclosure:  ventilated, NEMA 3R [NEMA 4][NEMA 4X][NEMA 12][other].  

L Enclosure Finish:  ANSI 61 Grey suitable for UL50 outdoor applications [other].
M Transformers shall terminate in either leads or mounting pads. Mounting lugs will be included on all units up to and including 270 amp ratings. Contractors shall provide all necessary lugs not already provided with transformer.
N UL listed, CSA approved, [CE Mark].
O Silicon Brass (or approved equivalent) hardware.
P UL Approved for Hazardous Locations [UL 1604 (Class 1, Division 2, Groups A,B,C,D and Class I, Zone 2, Group IIC, T3 Hazardous Location), (Temperature Classification equal to T3C/T3A]

Q Type ABS Approval for Marine Duty Service and Offshore Applications – Electric Distribution and Propulsion.
R Built to NEMA ST-20 and in accordance with all applicable UL, CSA and ANSI/IEEE standards.
S Seismic: transformers are designed and manufactured to comply with the specifications: International Building Code (IBC 2012), The California Building Code (CBC2013) and National Building Code of Canada (NBC 2010), OSHPD.
T Mounting: 

i Encapsulated units up to 285 lbs: Suitable for wall or floor mounting.
ii Encapsulated units over 285 lbs.: Suitable for floor mounting only.

Options:

· Type 316 Stainless Steel Enclosures
· Stainless Steel Nameplate
2.4 Acceptable Product and Manufacturer:
A HPS Titan® transformer, Hammond Power Solutions Inc. (Canada: 1-888-798-8882  /  U.S.: 1-866-705-4684).
B Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.
3 EXECUTION

3.1 Installation
A The installing contractor shall install the HPS Titan® Encapsulated Distribution Transformer per the manufacturer's recommended installation practices as found in the installation, operation, and maintenance manual and comply with all applicable codes.

B Make sure that the transformer is level.
C Check for damage and loose connections.
D Mount transformer to comply with all applicable codes.
E Install seismic restraint where indicated on the drawing.
F Coordinate all work in this section with all work of other sections.
G Take Infrared Picture to verify connections accuracy or deficiencies. 

H Prior to energizing transformer, verify secondary voltages and if necessary adjust secondary taps.
I Report for the Commission of the transformer shall include:
i Primary & Secondary Voltages

ii Primary & secondary THDi & THDv

PAGE  
CSI-2004 (Section 26 22 13)                                  
                         Page 4 of 4                              
                                           SPS# 09, Rev: 05

